## XR150 XR550
Job Name:
Installing Company:
XR150/XR550 SERIES STANDBY BATTERY POWER CALCULATIONS |  |  | Standby Current | [5 empty] | Alarm Current
|  |  | Qty |  | mA |  | Total mA |  | Qty |  | mA |  | Total mA
XR150/XR550 Series Control Panel |  |  | 1 | X | 174 | = | 174 |  | 1 | X | 217 | = | 217
Relay Outputs 1-2 (ON) |  |  | 0 | X | 30 | = | 0 |  | 0 | X | 30 | = | 0
Switching Grounds 3-6 (ON) |  |  | 0 | X | 5 | = | 0 |  | 0 | X | 5 | = | 0
Active Zones 1-8 |  |  | 0 | X | 1.6 | = | 0 |  | 0 | X | 2 | = | 0 | *
Active Zones 9-10 |  |  | 0 | X | 4 | = | 0 |  | 0 | X | 30 | = | 0 | *
2-Wire Smokes |  |  | 0 | X | 0.1 | = | 0 |  | 0 | X | 0.1 | = | 0 | *
Panel Bell Output (1500 mA max) | [10 empty] | 0 |  | 0
Aux. power devices on Terminals 7 and 11 (Other than keypads and LX-Bus modules) |  |  | 0 | X |  | = | 0 |  | 0 | X |  | = | 0 | *
2W‑BLX, 2WT‑BLX Smoke Detectors |  |  | 0 | X | 15 | = | 0 |  | 0 | X | 35 | = | 0
263LTE Cellular Communicator |  |  | 0 | X | 20 | = | 0 |  | 0 | X | 20 | = | 0
263LTE-FN Cellular Communicator |  |  | 0 | X | 20 | = | 0 |  | 0 | X | 20 | = | 0
277 Buzzer Module |  |  | 0 | X | 5 | = | 0 |  | 0 | X | 5 | = | 0
630F Remote Fire Command Center |  |  | 0 | X | 63 | = | 0 |  | 0 | X | 92 | = | 0
708 Bus Extender |  |  | 0 | X | 10 | = | 0 |  | 0 | X | 10 | = | 0
710 Bus Splitter/Repeater Module |  |  | 0 | X | 32 | = | 0 |  | 0 | X | 32 | = | 0
711 Zone Expansion Module |  |  | 0 | X | 11 | = | 0 |  | 0 | X | 11 | = | 0
Active Zone (EOL Installed) |  |  | 0 | X | 1.6 | = | 0 |  | 0 | X | 2 | = | 0
711S Zone Expansion Module |  |  | 0 | X | 4.2 | = | 0 |  | 0 | X | 4.7 | = | 0
712‑8 Zone Expansion Module |  |  | 0 | X | 17 | = | 0 |  | 0 | X | 17 | = | 0
Active Zones (EOL Installed) |  |  | 0 | X | 1.6 | = | 0 |  | 0 | X | 2 | = | 0
714 Zone Expansion Module |  |  | 0 | X | 7 | = | 0 |  | 0 | X | 7 | = | 0
Active Zones (EOL Installed) |  |  | 0 | X | 1.6 | = | 0 |  | 0 | X | 2 | = | 0
714‑8, 714‑16 Zone Expansion Module |  |  | 0 | X | 20 | = | 0 |  | 0 | X | 20 | = | 0
Active Zones (EOL Installed) |  |  | 0 | X | 1.6 | = | 0 |  | 0 | X | 2 | = | 0
715 Zone Expansion Module |  |  | 0 | X | 7 | = | 0 |  | 0 | X | 7 | = | 0
Active Zones (EOL Installed) |  |  | 0 | X | 4 | = | 0 |  | 0 | X | 30 | = | 0
2‑Wire Smokes |  |  | 0 | X | 0.1 | = | 0 |  | 0 | X | 0.1 | = | 0
715‑8, 715‑16 Zone Expansion Modules |  |  | 0 | X | 20 | = | 0 |  | 0 | X | 20 | = | 0
Active Zones (EOL Installed) |  |  | 0 | X | 4 | = | 0 |  | 0 | X | 30 | = | 0
2‑Wire Smokes |  |  | 0 | X | 0.1 | = | 0 |  | 0 | X | 0.1 | = | 0
716 Output Expansion Module |  |  | 0 | X | 13 | = | 0 |  | 0 | X | 13 | = | 0
Active Form C Relays |  |  | 0 | X |  | = | 0 |  | 0 | X | 12 | = | 0
717 Graphic Annunciator Module |  |  | 0 | X | 10 | = | 0 |  | 0 | X | 10 | = | 0
Annunciator Outputs |  |  | 0 | X |  | = | 0 |  | 0 | X | 1 | = | 0
734 Wiegand Interface Module |  |  | 0 | X | 40 | = | 0 |  | 0 | X | 60 | = | 0
Active Zones (EOL Installed) |  |  | 0 | X | 1.6 | = | 0 |  | 0 | X | 2 | = | 0
Annunciator (ON) |  |  | 0 | X |  | = | 0 |  | 0 | X | 20 | = | 0
Proximity Reader |  |  | 0 | X | 200 | = | 0 |  | 0 | X | 200 | = | 0
736P POPIT Interface Module |  |  | 0 | X | 25 | = | 0 |  | 0 | X | 25 | = | 0
Radionics Popex, Octopopit, Popits |  |  | 0 | X |  | = | 0 |  | 0 | X |  | = | 0
736V V-Plex Module |  |  | 0 | X | 45 | = | 0 |  | 0 | X | 45 | = | 0
Active Zones |  |  | 0 | X |  | = | 0 |  | 0 | X |  | = | 0
738A Ademco Wireless Interface Module |  |  | 0 | X | 75 | = | 0 |  | 0 | X | 75 | = | 0
738T Wireless Translator |  |  | 0 | X | 50 | = | 0 |  | 0 | X | 50 | = | 0
738Zplus Z-Wave Interface Module |  |  | 0 | X | 40 | = | 0 |  | 0 | X | 40 | = | 0
763 Wi-Fi Module |  |  | 0 | X | 31 | = | 0 |  | 0 | X | 31 | = | 0
860 Relay Output Module, one relay active |  |  | 0 | X | 34 | = | 0 |  | 0 | X | 34 | = | 0
All four relays active |  |  | 0 | X | 138 | = | 0 |  | 0 | X | 138 | = | 0
865 Style Y or Z Notification Module |  |  | 0 | X | 26 | = | 0 |  | 0 | X | 85 | = | 0
866 Style W Notification Module |  |  | 0 | X | 45 | = | 0 |  | 0 | X | 76 | = | 0
867 LX‑Bus Style W Notification Module |  |  | 0 | X | 30 | = | 0 |  | 0 | X | 86 | = | 0
869 Dual Style D Initiating Module |  |  | 0 | X | 25 | = | 0 |  | 0 | X | 75 | = | 0
893A Dual Phone Line Module |  |  | 0 | X | 12 | = | 0 |  | 0 | X | 50 | = | 0
1100X Wireless Receiver |  |  | 0 | X | 25 | = | 0 |  | 0 | X | 35 | = | 0
1100XH Wireless High Power Receiver |  |  | 0 | X | 75 | = | 0 |  | 0 | X | 102 | = | 0
7060/7160 Thinline/7060A Aqualite Keypad |  |  | 0 | X | 72 | = | 0 |  | 0 | X | 87 | = | 0
7063/7163 Thinline/7063A Aqualite Keypad |  |  | 0 | X | 85 | = | 0 |  | 0 | X | 100 | = | 0
7070/7170 Thinline/7070A Aqualite Keypad |  |  | 0 | X | 72 | = | 0 |  | 0 | X | 87 | = | 0
Active Zones (EOL Installed) |  |  | 0 | X | 1.6 | = | 0 |  | 0 | X | 2 | = | 0
7073/7173 Thinline/7073A Aqualite Keypad |  |  | 0 | X | 85 | = | 0 |  | 0 | X | 100 | = | 0
Active Zones (EOL Installed) |  |  | 0 | X | 1.6 | = | 0 |  | 0 | X | 2 | = | 0
7872 Graphic Touchscreen Keypad |  |  | 0 | X | 145 | = | 0 |  | 0 | X | 215 | = | 0
Active Zones (EOL Installed) |  |  | 0 | X | 1.6 | = | 0 |  | 0 | X | 2 | = | 0
7873 Graphic Touchscreen Keypad |  |  | 0 | X | 143 | = | 0 |  | 0 | X | 243 | = | 0
Active Zones (EOL Installed) |  |  | 0 | X | 1.6 | = | 0 |  | 0 | X | 2 | = | 0
Aux. Powered Devices |  |  | 0 | X |  | = | 0 |  | 0 | X |  | = | 0 | *
Aux. Powered Devices |  |  | 0 | X |  | = | 0 |  | 0 | X |  | = | 0 | *
Aux. Powered Devices |  |  | 0 | X |  | = | 0 |  | 0 | X |  | = | 0 | *
Aux. Powered Devices |  |  | 0 | X |  | = | 0 |  | 0 | X |  | = | 0 | *
Aux. Powered Devices |  |  | 0 | X |  | = | 0 |  | 0 | X |  | = | 0 | *
Aux. Powered Devices |  |  | 0 | X |  | = | 0 |  | 0 | X |  | = | 0 | *
Aux. Powered Devices |  |  | 0 | X |  | = | 0 |  | 0 | X |  | = | 0 | *
Aux. Powered Devices |  |  | 0 | X |  | = | 0 |  | 0 | X |  | = | 0 | *
Aux. Powered Devices |  |  | 0 | X |  | = | 0 |  | 0 | X |  | = | 0 | *
* Based on 10% active zones in alarm |  |  |  |  | Total Standby mA |  | 174 |  |  |  | Total Alarm mA |  | 217
| Required Minimum Alarm Time in minutes |  |  |  | 0 | Minutes | X Total Alarm mA | 217 | = | Total Required Alarm Current |  |  | 0 | mAh
[6 empty] | Total Standby mA |  |  |  | 174 | mA
[6 empty] | Number of standby hours needed |  |  | * | 24 | h
[6 empty] | Total number of standby mA hours |  |  | = | 4176 | mAh
[6 empty] | Total required alarm current (rounded) |  |  | + | 0 | mAh
[6 empty] | Total number of mA hours |  |  | = | 4176 | mAh | 1 |  |  | 0
[6 empty] | Contingency factor |  |  | + | 20 | %
[6 empty] | Total number of mAh |  |  | = | 5011.2 | mAh
[6 empty] | Convert mAh to Ah |  |  | ÷ | 1000 | h
[6 empty] | Battery Amp hours required |  |  | = | 6 | Ah
For more information, refer to the Standby Battery Selection section of the XR150/XR550 Series Installation Guide (LT-1233).
This spreadsheet calculator has not been evaluated by UL.
DMP is not responsible for errors, omissions, or inaccuracies.
©2023 23462
Note on H86: For UL installations, refer to XR150/XR550 Installation Manual for transformer selection to match your application. Type of installation and transformer model determines Aux. Power output and Bell output as well as number and size of batteries.
Note on K106: Refer to the XR150/XR550 Install Guide (LT-1233) for proper transformer depending on number of batteries used
Set All to Zero

## XF6
Job Name:
Installing Company:
XF6 SERIES STANDBY BATTERY POWER CALCULATIONS |  |  | Standby Current | [5 empty] | Alarm Current
|  |  | Qty |  | mA |  | Total mA |  | Qty |  | mA |  | Total mA
XF6 Series Control Panel |  |  | 1 | X | 90 | = | 90 |  | 1 | X | 102 | = | 102
Fire Command Keypad |  |  | 1 | X | 84 | = | 84 |  | 1 | x | 108 | = | 108
Relay Outputs (ON) |  |  | 0 | X | 3 | = | 0 |  | 0 | X | 3 | = | 0
Switching Grounds (ON) |  |  | 0 | X | 7 | = | 0 |  | 0 | X | 61 | = | 0
Active Zones |  |  | 0 | X | 7 | = | 0 |  | 0 | X | 7 | = | 0 | *
NAC Zones |  |  | 0 | X |  | = | 0 |  | 0 | X |  | = | 0
2-Wire Smoke Detectors |  |  | 0 | X |  | = | 0 |  | 0 | X |  | = | 0 | *
263LTE Cellular Communicator |  |  | 0 | X | 12 | = | 0 |  | 0 | X | 12 | = | 0
1100X Wireless Receiver |  |  | 0 | X | 15 | = | 0 |  | 0 | X | 21 | = | 0
1100XH Wireless High Power Receiver |  |  | 0 | X | 45 | = | 0 |  | 0 | X | 61 | = | 0
7830F Fire Command Keypad |  |  | 0 | X | 84 | = | 0 |  | 0 | X | 108 | = | 0
630F Remote Fire Command Center |  |  | 0 | X | 38 | = | 0 |  | 0 | X | 55 | = | 0
7070/7170 Thinline/7070A Aqualite Keypad |  |  | 0 | X | 43 | = | 0 |  | 0 | X | 52 | = | 0
Active Zones (EOL Installed) |  |  | 0 | X | 1 | = | 0 |  | 0 | X | 1 | = | 0
7073/7173 Thinline/7073A Aqualite Keypad |  |  | 0 | X | 51 | = | 0 |  | 0 | X | 60 | = | 0
Active Zones (EOL Installed) |  |  | 0 | X | 1 | = | 0 |  | 0 | X | 1 | = | 0
710 Bus Splitter/Repeater Module |  |  | 0 | X | 19 | = | 0 |  | 0 | X | 19 | = | 0
711/711S Zone Expansion Module |  |  | 0 | X | 7 | = | 0 |  | 0 | X | 7 | = | 0
Active Zone (EOL Installed) |  |  | 0 | X | 1 | = | 0 |  | 0 | X | 1 | = | 0
714 Zone Expansion Module |  |  | 0 | X | 4 | = | 0 |  | 0 | X | 4 | = | 0
Active Zones (EOL Installed) |  |  | 0 | X | 1 | = | 0 |  | 0 | X | 2 | = | 0
714‑8, 714‑16 Zone Expansion Module |  |  | 0 | X | 12 | = | 0 |  | 0 | X | 12 | = | 0
Active Zones (EOL Installed) |  |  | 0 | X | 1 | = | 0 |  | 0 | X | 1 | = | 0
715 Zone Expansion Module |  |  | 0 | X | 4 | = | 0 |  | 0 | X | 4 | = | 0
Active Zones (EOL Installed) |  |  | 0 | X | 2 | = | 0 |  | 0 | X | 34 | = | 0
2‑Wire Smokes |  |  | 0 | X | 0.1 | = | 0 |  | 0 | X | 18 | = | 0
715‑8, 715‑16 Zone Expansion Modules |  |  | 0 | X | 12 | = | 0 |  | 0 | X | 12 | = | 0
Active Zones (EOL Installed) |  |  | 0 | X | 2 | = | 0 |  | 0 | X | 34 | = | 0
2‑Wire Smokes |  |  | 0 | X | 0.1 | = | 0 |  | 0 | X | 18 | = | 0
716 Output Expansion Module |  |  | 0 | X | 4 | = | 0 |  | 0 | X | 4 | = | 0
Active Form C Relays |  |  | 0 | X |  | = | 0 |  | 0 | X | 17 | = | 0
860 Relay Output Module (one relay active) |  |  | 0 | X | 20 | = | 0 |  | 0 | X | 20 | = | 0
All four relays active |  |  | 0 | X | 83 | = | 0 |  | 0 | X | 83 | = | 0
865 Class A or B Notification Module |  |  | 0 | X | 16 | = | 0 |  | 0 | X | 51 | = | 0
866 Class B Notification Module |  |  | 0 | X | 27 | = | 0 |  | 0 | X | 46 | = | 0
867 LX‑Bus Class B Notification Module |  |  | 0 | X | 18 | = | 0 |  | 0 | X | 52 | = | 0
2W‑BLX, 2WT‑BLX Smoke Detectors |  |  | 0 | X | 9 | = | 0 |  | 0 | X | 21 | = | 0
COSMOD2W Module |  |  | 0 | X | 27 | = | 0 |  | 0 | X | 104 | = | 0
COSMO-2W Smoke and CO Detectors |  |  | 0 | X | 0.6 | = | 0 |  | 0 | X | 30 | = | 0
572 Indicator LED |  |  | 0 | X | 12 | = | 0 |  | 0 | X | 12 | = | 0
Aux. Powered Devices on Terminals 7 and 11 Other than Keypads and LX-Bus Modules |  |  | 0 | X |  | = | 0 |  | 0 | X |  | = | 0 | *
*
* Based on 10% active zones in alarm |  |  |  |  | Total Standby mA |  | 174 |  |  |  | Total Alarm mA |  | 210
| Required Minimum Alarm Time in minutes |  |  |  | 0 | Minutes | X Total Alarm mA | 210 | = | Total Required Alarm Current |  |  | 0
mAh
[6 empty] | Total Standby mA |  |  |  | 174 | mA
[6 empty] | Number of standby hours needed |  |  | * | 24 | h
[6 empty] | Total number of standby mA hours |  |  | = | 4176 | mAh
[6 empty] | Total required alarm current (rounded) |  |  | + | 0 | mAh
[6 empty] | Total number of mA hours |  |  | = | 4176 | mAh | 1
[6 empty] | Contingency factor |  |  | + | 20 | % |  |  |  | 0
[6 empty] | Total number of mAh |  |  | = | 5011.2 | mAh
[6 empty] | Convert mAh to Ah |  |  | ÷ | 1000 | h
[6 empty] | Battery Amp hours required |  |  | = | 6 | Ah
For more information, refer to the Standby Battery Selection section of the XR150/XR550 Series Installation Guide (LT-1233).
This spreadsheet calculator has not been evaluated by UL.
DMP is not responsible for errors, omissions, or inaccuracies.
©2023 23462
Set All to Zero

## XT30 XT50
Job Name:
Installing Company:
XT30/XT50 SERIES STANDBY BATTERY POWER CALCULATIONS |  | Standby Current | [5 empty] | Alarm Current
|  | Qty |  | mA |  | Total mA |  | Qty |  | mA |  | Total mA
XT30 Series Control Panel |  | 0 | X | 125 | = | 0 |  | 0 | X | 125 | = | 0
Built-in network (additional current) |  | 0 | X | 145 | = | 0 |  | 0 | X | 145 | = | 0
Active Zones 1-9 |  | 0 | X | 1.6 | = | 0 |  | 0 | X | 2 | = | 0
Active Zones 10 |  | 0 | X | 4 | = | 0 |  | 0 | X | 30 | = | 0
2-Wire Smokes |  | 0 | X | 0.1 | = | 0 |  | 0 | X | 0.1 | = | 0
Panel Bell Output (1500 mA max) |  | 0 | [7 empty] | 0 |  | 0
Aux. power devices on Terminals 7 and 11 (Other than keypads and LX-Bus modules) |  | 0 | X |  | = | 0 |  | 0 | X |  | = | 0
XT50 Series Control Panel |  | 0 | X | 145 | = | 0 |  | 0 | X | 145 | = | 0
Built-in network (additional current) |  | 0 | X | 145 | = | 0 |  | 0 | X | 145 | = | 0
Active Zones 1-9 |  | 0 | X | 1.6 | = | 0 |  | 0 | X | 2 | = | 0
Active Zones 10 |  | 0 | X | 4 | = | 0 |  | 0 | X | 30 | = | 0
2-Wire Smokes |  | 0 | X | 0.1 | = | 0 |  | 0 | X | 0.1 | = | 0
Panel Bell Output (1500 mA max) | [9 empty] | 0 |  | 0
Aux. power devices on Terminals 7 and 11 (Other than keypads and LX-Bus modules) |  | 0 | X |  | = | 0 |  | 0 | X |  | = | 0
263LTE Cellular Communicator |  | 0 | X | 20 | = | 0 |  | 0 | X | 20 | = | 0
708 Bus Extender |  | 0 | X | 10 | = | 0 |  | 0 | X | 10 | = | 0
710 Bus Splitter/Repeater Module |  | 0 | X | 32 | = | 0 |  | 0 | X | 32 | = | 0
711 Zone Expansion Module |  | 0 | X | 11 | = | 0 |  | 0 | X | 11 | = | 0
Active Zone (EOL Installed) |  | 0 | X | 1.6 | = | 0 |  | 0 | X | 2 | = | 0
711S Zone Expansion Module |  | 0 | X | 4.2 | = | 0 |  | 0 | X | 4.7 | = | 0
712‑8 Zone Expansion Module |  | 0 | X | 17 | = | 0 |  | 0 | X | 17 | = | 0
Active Zones (EOL Installed) |  | 0 | X | 1.6 | = | 0 |  | 0 | X | 2 | = | 0
714 Zone Expansion Module |  | 0 | X | 7 | = | 0 |  | 0 | X | 7 | = | 0
Active Zones (EOL Installed) |  | 0 | X | 1.6 | = | 0 |  | 0 | X | 2 | = | 0
714‑8, 714‑16 Zone Expansion Module |  | 0 | X | 20 | = | 0 |  | 0 | X | 20 | = | 0
Active Zones (EOL Installed) |  | 0 | X | 1.6 | = | 0 |  | 0 | X | 2 | = | 0
715 Zone Expansion Module |  | 0 | X | 7 | = | 0 |  | 0 | X | 7 | = | 0
Active Zones (EOL Installed) |  | 0 | X | 4 | = | 0 |  | 0 | X | 30 | = | 0
2‑Wire Smokes |  | 0 | X | 0.1 | = | 0 |  | 0 | X | 0.1 | = | 0
715‑8, 715‑16 Zone Expansion Modules |  | 0 | X | 20 | = | 0 |  | 0 | X | 20 | = | 0
Active Zones (EOL Installed) |  | 0 | X | 4 | = | 0 |  | 0 | X | 30 | = | 0
2‑Wire Smokes |  | 0 | X | 0.1 | = | 0 |  | 0 | X | 0.1 | = | 0
736P POPIT Interface Module |  | 0 | X | 25 | = | 0 |  | 0 | X | 25 | = | 0
738A Ademco Wireless Interface Module |  | 0 | X | 75 | = | 0 |  | 0 | X | 75 | = | 0
738T Wireless Translator |  | 0 | X | 50 | = | 0 |  | 0 | X | 50 | = | 0
738Zplus Z-Wave Interface Module |  | 0 | X | 40 | = | 0 |  | 0 | X | 40 | = | 0
763 Wi-Fi Module |  | 0 | X | 31 | = | 0 |  | 0 | X | 31 | = | 0
860 Relay Output Module, one relay active |  | 0 | X | 34 | = | 0 |  | 0 | X | 34 | = | 0
All four relays active |  | 0 | X | 138 | = | 0 |  | 0 | X | 138 | = | 0
865 Style Y or Z Notification Module |  | 0 | X | 26 | = | 0 |  | 0 | X | 85 | = | 0
866 Style W Notification Module |  | 0 | X | 45 | = | 0 |  | 0 | X | 76 | = | 0
1100D Wireless Receiver |  | 0 | X | 40 | = | 0 |  | 0 | X | 40 | = | 0
1100DH High-Powered Wireless Receiver |  | 0 | X | 240 | = | 0 |  | 0 | X | 240 | = | 0
1100DI In-Line Wireless Receiver |  | 0 | X | 35 | = | 0 |  | 0 | X | 35 | = | 0
7060/7160 Thinline/7060A Aqualite Keypad |  | 0 | X | 72 | = | 0 |  | 0 | X | 80 | = | 0
7063/7163 Thinline/7063A Aqualite Keypad |  | 0 | X | 85 | = | 0 |  | 0 | X | 100 | = | 0
7070/7170 Thinline/7070A Aqualite Keypad |  | 0 | X | 72 | = | 0 |  | 0 | X | 87 | = | 0
Active Zones (EOL Installed) |  | 0 | X | 1.6 | = | 0 |  | 0 | X | 2 | = | 0
7073/7173 Thinline/7073A Aqualite Keypad |  | 0 | X | 85 | = | 0 |  | 0 | X | 100 | = | 0
Active Zones (EOL Installed) |  | 0 | X | 1.6 | = | 0 |  | 0 | X | 2 | = | 0 | *
7872 Graphic Touchscreen Keypad |  | 0 | X | 145 | = | 0 |  | 0 | X | 215 | = | 0 | *
Active Zones (EOL Installed) |  | 0 | X | 1.6 | = | 0 |  | 0 | X | 2 | = | 0 | *
7873 Graphic Touchscreen Keypad |  | 0 | X | 143 | = | 0 |  | 0 | X | 243 | = | 0
Active Zones (EOL Installed) |  | 0 | X | 1.6 | = | 0 |  | 0 | X | 2 | = | 0 | *
Aux. Powered Devices |  | 0 | X | 15 | = | 0 |  | 0 | X | 15 | = | 0 | *
Aux. Powered Devices |  | 0 | X |  | = | 0 |  | 0 | X |  | = | 0 | *
Aux. Powered Devices |  | 0 | X |  | = | 0 |  | 0 | X |  | = | 0 | *
Aux. Powered Devices |  | 0 | X |  | = | 0 |  | 0 | X |  | = | 0 | *
Aux. Powered Devices |  | 0 | X |  | = | 0 |  | 0 | X |  | = | 0 | *
Aux. Powered Devices |  | 0 | X |  | = | 0 |  | 0 | X |  | = | 0 | *
Aux. Powered Devices |  | 0 | X |  | = | 0 |  | 0 | X |  | = | 0 | *
Aux. Powered Devices |  | 0 | X |  | = | 0 |  | 0 | X |  | = | 0 | *
Aux. Powered Devices |  | 0 | X |  | = | 0 |  | 0 | X |  | = | 0 | *
* Based on 10% active zones in alarm |  |  |  | Total Standby mA |  | 0 |  |  |  | Total Alarm mA |  | 0
| Required Minimum Alarm Time in minutes |  |  | 0 | Minutes | X Total Alarm mA | 0 | mA | = | Total Required Alarm Current |  |  | 0 | mAh
[5 empty] | Total Standby mA |  |  |  | 0 | mA
[5 empty] | Number of standby hours needed |  |  | * | 24 | h
[5 empty] | Total number of standby mA hours |  |  | = | 0 | mAh
[5 empty] | Total required alarm current (rounded) |  |  | + | 0 | mAh
[5 empty] | Total number of mA hours |  |  | = | 0 | mAh | 1
[5 empty] | Contingency factor |  |  | + | 0 | %
[5 empty] | Total number of mAh |  |  | = | 0 | mAh
[5 empty] | Convert mAh to Ah |  |  | ÷ | 1000 | h
[5 empty] | Battery Amp hours required |  |  | = | 0 | Ah
For more information, refer to the Standby Battery Selection section of the XT30/XT50 Series Installation Guide (LT-0980).
This spreadsheet calculator has not been evaluated by UL.
DMP is not responsible for errors, omissions, or inaccuracies.
©2023 23462
Note on D46: Max. 1 per panel
Note on D52: Only used with XT30 panels without built-in wireless
Note on D53: Only used with XT30 panels without built-in wireless
Note on D54: Only used with XT30 panels without built-in wireless
Note on K94: Refer to the XR150/XR550 Install Guide (LT-1233) for proper transformer depending on number of batteries used
Set All to Zero

## 505-12
Job Name:
Installing Company:
505-12 STANDBY BATTERY POWER CALCULATIONS |  | Standby Current | [5 empty] | Alarm Current
|  | Qty |  | mA |  | Total mA |  | Qty |  | mA |  | Total mA
505-12 Power Supply |  | 1 | X | 200 | = | 200 |  | 1 | X | 200 | = | 200
DualComNF |  | 0 | X | 64 | = | 0 |  | 0 | X | 109 | = | 0
2W‑BLX, 2WT‑BLX Smoke Detectors |  | 0 | X | 11 | = | 0 |  | 0 | X | 31 | = | 0
630F Remote Fire Command Center |  | 0 | X | 63 | = | 0 |  | 0 | X | 92 | = | 0
708 Bus Extender |  | 0 | X | 10 | = | 0 |  | 0 | X | 10 | = | 0
710 Bus Splitter/Repeater Module |  | 0 | X | 32 | = | 0 |  | 0 | X | 32 | = | 0
711 Zone Expansion Module |  | 0 | X | 11 | = | 0 |  | 0 | X | 11 | = | 0
Active Zone (EOL Installed) |  | 0 | X | 1.6 | = | 0 |  | 0 | X | 2 | = | 0
711S Zone Expansion Module |  | 0 | X | 4.2 | = | 0 |  | 0 | X | 4.7 | = | 0
712‑8 Zone Expansion Module |  | 0 | X | 17 | = | 0 |  | 0 | X | 17 | = | 0
Active Zones (EOL Installed) |  | 0 | X | 1.6 | = | 0 |  | 0 | X | 2 | = | 0
714 Zone Expansion Module |  | 0 | X | 7 | = | 0 |  | 0 | X | 7 | = | 0
Active Zones (EOL Installed) |  | 0 | X | 1.6 | = | 0 |  | 0 | X | 2 | = | 0
714‑8, 714‑16 Zone Expansion Module |  | 0 | X | 20 | = | 0 |  | 0 | X | 20 | = | 0
Active Zones (EOL Installed) |  | 0 | X | 1.6 | = | 0 |  | 0 | X | 2 | = | 0
715 Zone Expansion Module |  | 0 | X | 7 | = | 0 |  | 0 | X | 7 | = | 0
Active Zones (EOL Installed) |  | 0 | X | 4 | = | 0 |  | 0 | X | 30 | = | 0
2‑Wire Smokes |  | 0 | X | 0.1 | = | 0 |  | 0 | X | 0.1 | = | 0
715‑8, 715‑16 Zone Expansion Modules |  | 0 | X | 20 | = | 0 |  | 0 | X | 20 | = | 0
Active Zones (EOL Installed) |  | 0 | X | 4 | = | 0 |  | 0 | X | 30 | = | 0
2‑Wire Smokes |  | 0 | X | 0.1 | = | 0 |  | 0 | X | 0.1 | = | 0
716 Output Expansion Module |  | 0 | X | 13 | = | 0 |  | 0 | X | 13 | = | 0
Active Form C Relays |  | 0 | X |  | = | 0 |  | 0 | X | 12 | = | 0
717 Graphic Annunciator Module |  | 0 | X | 10 | = | 0 |  | 0 | X | 10 | = | 0
Annunciator Outputs |  | 0 | X |  | = | 0 |  | 0 | X | 1 | = | 0
734 Wiegand Interface Module |  | 0 | X | 240 | = | 0 |  | 0 | X | 260 | = | 0
Active Zones (EOL Installed) |  | 0 | X | 1.6 | = | 0 |  | 0 | X | 2 | = | 0
Annunciator (ON) |  | 0 | X |  | = | 0 |  | 0 | X | 20 | = | 0
Proximity Reader |  | 0 | X | 200 | = | 0 |  | 0 | X | 200 | = | 0
736P POPIT Interface Module |  | 0 | X | 25 | = | 0 |  | 0 | X | 25 | = | 0
736V V-Plex Module |  | 0 | X | 45 | = | 0 |  | 0 | X | 45 | = | 0
Active Zones |  | 0 | X |  | = | 0 |  | 0 | X |  | = | 0
738A Ademco Wireless Interface Module |  | 0 | X | 75 | = | 0 |  | 0 | X | 75 | = | 0
738T Wireless Translator |  | 0 | X | 50 | = | 0 |  | 0 | X | 50 | = | 0
738Zplus Z-Wave Interface Module |  | 0 | X | 40 | = | 0 |  | 0 | X | 40 | = | 0
763 Wi-Fi Module |  | 0 | X | 31 | = | 0 |  | 0 | X | 31 | = | 0
860 Relay Output Module, one relay active |  | 0 | X | 34 | = | 0 |  | 0 | X | 34 | = | 0
All four relays active |  | 0 | X | 138 | = | 0 |  | 0 | X | 138 | = | 0
865 Style Y or Z Notification Module |  | 0 | X | 26 | = | 0 |  | 0 | X | 85 | = | 0
866 Style W Notification Module |  | 0 | X | 45 | = | 0 |  | 0 | X | 76 | = | 0
867 LX‑Bus Style W Notification Module |  | 0 | X | 30 | = | 0 |  | 0 | X | 86 | = | 0
869 Dual Style D Initiating Module |  | 0 | X | 25 | = | 0 |  | 0 | X | 75 | = | 0
893A Dual Phone Line Module |  | 0 | X | 12 | = | 0 |  | 0 | X | 50 | = | 0
1100D Wireless Receiver |  | 0 | X | 40 | = | 0 |  | 0 | X | 40 | = | 0
1100DH High-Powered Wireless Receiver |  | 0 | X | 240 | = | 0 |  | 0 | X | 240 | = | 0
1100DI In-Line Wireless Receiver |  | 0 | X | 35 | = | 0 |  | 0 | X | 35 | = | 0
1100X Wireless Receiver |  | 0 | X | 46 | = | 0 |  | 0 | X | 46 | = | 0
1100XH Wireless High Power Receiver |  | 0 | X | 160 | = | 0 |  | 0 | X | 160 | = | 0
7060/7160 Thinline/7060A Aqualite Keypad |  | 0 | X | 72 | = | 0 |  | 0 | X | 80 | = | 0
7063/7163 Thinline/7063A Aqualite Keypad |  | 0 | X | 85 | = | 0 |  | 0 | X | 100 | = | 0
7070/7170 Thinline/7070A Aqualite Keypad |  | 0 | X | 72 | = | 0 |  | 0 | X | 87 | = | 0
Active Zones (EOL Installed) |  | 0 | X | 1.6 | = | 0 |  | 0 | X | 2 | = | 0
7073/7173 Thinline/7073A Aqualite Keypad |  | 0 | X | 85 | = | 0 |  | 0 | X | 100 | = | 0
Active Zones (EOL Installed) |  | 0 | X | 1.6 | = | 0 |  | 0 | X | 2 | = | 0
7872 Graphic Touchscreen Keypad |  | 0 | X | 145 | = | 0 |  | 0 | X | 215 | = | 0
Active Zones (EOL Installed) |  | 0 | X | 1.6 | = | 0 |  | 0 | X | 2 | = | 0
7873 Graphic Touchscreen Keypad |  | 0 | X | 143 | = | 0 |  | 0 | X | 243 | = | 0
Active Zones (EOL Installed) |  | 0 | X | 1.6 | = | 0 |  | 0 | X | 2 | = | 0
Aux. Powered Devices |  | 0 | X |  | = | 0 |  | 0 | X |  | = | 0 | *
Aux. Powered Devices |  | 0 | X |  | = | 0 |  | 0 | X |  | = | 0 | *
Aux. Powered Devices |  | 0 | X |  | = | 0 |  | 0 | X |  | = | 0 | *
* Based on 10% active zones in alarm |  |  |  | Total Standby mA |  | 200 |  |  |  | Total Alarm mA |  | 200
| Required Minimum Alarm Time in minutes |  | 0 | 0 | Minutes | X Total Alarm mA | 200 | mA | = | Total Required Alarm Current |  |  | 0 | mAh
[5 empty] | Total Standby mA |  |  |  | 200 | mA
[5 empty] | Number of standby hours needed |  |  | * | 24 | h
[5 empty] | Total number of standby mA hours |  |  | = | 4800 | mAh
[5 empty] | Total required alarm current (rounded) |  |  | + | 0 | mAh
[5 empty] | Total number of mA hours |  |  | = | 4800 | mAh | 1
[5 empty] | Contingency factor |  |  | + | 0 | %
[5 empty] | Total number of mAh |  |  | = | 4800 | mAh
[5 empty] | Convert mAh to Ah |  |  | ÷ | 1000 | h
[5 empty] | Battery Amp hours required |  |  | = | 5 | Ah
For more information, refer to the Standby Battery Selection section of the 505-12 Installation Guide (LT-0453).
This spreadsheet calculator has not been evaluated by UL.
DMP is not responsible for errors, omissions, or inaccuracies.
©2023 23462
Note on K93: Refer to the 505-12 Install Guide (LT-0453) for proper transformer depending on number of batteries used
Set All to Zero